PRODUCT  DATA  SHEET

G

SENTI-THERM™

HEAT TRANSFER FLUID

HIGH TEMPERATURE

PRODUCT  DESCRIPTION

Sentinel’s SENTI-THERM™ is a synthetic liquid phase heat transfer fluid designed for use at moderate operating temperatures in non-pressurized indirect heating systems.  It resists chemical and physical change at all temperatures below its maximum bulk operating temperature of 315°C (600°F).

Sentinel’s SENTI-THERM™ major advantages of systems using fluids over mineral oils are greater versatility in operating temperature, better chemical stability, reduced make-up, and closer control of and faster response to temperature change as required by the operation.  
SENTI-THERM™ heat transfer fluid generally has greater heat carrying capacities and more practical viscosities over its temperature

TYPICAL  CHARACTERISTICS

range than minerals oils, little thermal degradation, and can provide long trouble-free service. 
 SENTI-THERM™  other advantages include better pumpability, high heat carrying capacity, low pour point, thermal and chemical stability, low vapor pressure, etc.

When not subjected to contamination, such as moisture, air, process material, or heat stress beyond its limit Sentinel’s SENTI-THERM™ can give years of service without significant physical or chemical change.

ISO Viscosity Grade					46					ASTM D-2422

SAE Viscosity Number					20					SAE     J-   300

Viscosity  cSt @100°C				             8.3					ASTM D-  445

@  40°C				           47.1

Viscosity Index					            152					ASTM D-2270

Pour Point °C (°F), Maximum			       -40 (-40)					ASTM D-    97

Flash Point °C (°F), C.O.C.			      243 (470)					ASTM D-    92

Foam Sequence I, II, III				           Nil					ASTM D-  892

Demulsibility 54.4°C (130°F)			    40/40/0 (15)					ASTM D-1401

Copper Corrosion 121°C (250°F)			          1a						ASTM D-  130

3 hrs

Conradson Carbon Residue %			         .02						ASTM D-  189

Autoignition Temperature °C (°F)			       400/750					ASTM D-2155

Appearance					Reddish Amber liquid

PIN #												       08201

ISO33

TO ORDER or FOR ADDITIONAL INFORMATION

PRODUCT  DATA  SHEET

SENTI-THERM™

HEAT TRANSFER FLUID

HIGH TEMPERATURE

SUPPLEMENTAL INFORMATION

THERMAL DATA

| PROPERTY | TEMPERATURE |  |  |  |
| --- | --- | --- | --- | --- |
|  | 15°C (59°F) | 38°C (100°F) | 260°C (500°F) | 316°C (600°F) |
| Thermal Conductivity, W/m K (BTU/hr. °F. ft) | 0.142 (0.082) | 0.141 (0.082) | 0.130 (0.075) | 0.127 (0.073) |
| Heat Capacity, kJ/kg K (BTU/lb. °F) | 1.89 (0.45) | 1.96 (0.47) | 2.69 (0.64) | 2.88 (0.69) |
| Vapour Pressure, kPa (psia) | 0.00 (0.00) | 0.00 (0.00) | 3.78 (0.55) | 15.32 (2.20) |
| Density, kg/L (lb/ft³) | 0.867 (54.1) | 0.852 (53.2) | 0.715 (44.7) | 0.681 (42.5) |

TO ORDER or FOR ADDITIONAL INFORMATION